** NOTE TO SPECIFIER **  This document is subject to copyright protection and is property of Ruskin Company.  Ruskin authorizes the Specifier a limited non-exclusive license to use this document (in whole or in part) for the purpose of preparing written product specifications for the above CSI MasterFormat category.  Ruskin Company is providing the information contained in this document for informational use, and is provided without representation or warranty of any kind as to the user or any other party, including, without limitation, any implied warranty of merchantability, and fitness for particular purpose, application, or non-infringement. To the greatest extent permitted by applicable law, Ruskin Company assumes no liability, and User assumes all liability and risk, for the use or results from the use of this document or the information contained herein, whether modified by the user or not. Any user of this document should consult www.ruskin.com to verify that the information contained herein is the most current representation of the specified product.

SECTION 08 91 00

EXTREME PERFORMANCE LOUVERS

Display hidden notes to specifier by using “Tools”/”Options”/“View”/”Hidden Text”.

** NOTE TO SPECIFIER **  This section is based on the products of Ruskin Company, which is located at:

3900 Dr. Greaves Road

Kansas City, Missouri 64030

Tel: (816) 761-7476

Fax: (816) 765-8955

Email: ruskin@ruskin.com

Web: http://www.ruskin.com

Ruskin Manufacturing has been the leading manufacturer of dampers and louvers for over 50 years. Ruskin has pioneered advanced products for the HVAC Industry and continues to be an industry leader with modern manufacturing equipment, computer-aided design capabilities and an AMCA registered air performance testing laboratory for research and development. All of these are backed by our experienced engineers and professional staff and reflects Ruskin's commitment to high quality product standards.

While providing fresh air intake and exhaust, Ruskin Louvers can also provide architectural style to building design. With the variety of models, sizes, and finishes available, Ruskin Louvers can add unusual and appealing features to exterior and interior elevations. Ruskin louvers are available in depths ranging from 1.5 inches to 12 inches, and can accommodate various blade angles with high free area.

SECTION 08 91 00, Copyright 2015, Ruskin Company.

GENERAL

SECTION INCLUDES

** NOTE TO SPECIFIER **  This section covers Ruskin Company HZ700MD extreme performance  louver.  Consult Ruskin Company representative for assistance in editing this section for specific applications.

AMCA540/550, extreme performance water, air, and wind driven rain Miami-Dade listed louver

RELATED SECTIONS

** NOTE TO SPECIFIER **  Delete any sections below not relevant to this project; add others as required.

Section 01 81 13 – USGBC LEED® Requirements.

Section 03 30 00 - Cast-In-Place Concrete.

Section 04 20 00 - Masonry Units.

Section 05 10 00 - Structural Metal Framing.

Section 06 10 00 - Rough Carpentry.

Section 07 42 00 - Metal Wall Panels.

Section 07 60 00 - Flashing and Sheet Metal.

Section 07 92 00 - Joint Sealants.

Section 09 91 00 - Paints.

Section 23 37 00 - Air Outlets and Inlets.

Section 23 33 13 – Dampers.

Section 23 09 13 – Instrumentation and Control Devices for HVAC.

REFERENCES

** NOTE TO SPECIFIER **  Delete references from the list below that are not actually required by the text of the edited section.

AAMA 2604 – High Performance Organic Coatings on Architectural Extrusions and Panels.

AAMA 2605 - High Performance Organic Coatings on Architectural Extrusions and Panels.

AAMA 611 – Voluntary Specification for anodized Architectural Aluminum.

AMCA 500L - Test Methods for Louvers, Dampers and Shutters.

AMCA 511 - Certified Ratings Program for Air Control Devices.

AMCA 540 – Test Method for Louvers Impacted by Windborne Debris. – Enhanced Protection.

AMCA 550 – High Velocity Wind Driven Rain Resistant Louvers.

ASCE 7 - Minimum Design Loads for Buildings and Other Structures.

ASTM D822 - Standard Practice for Filtered Open-Flame Carbon-Arc Exposures of Paint and Related Coatings

ASTM D4214 - Standard Test Methods for Evaluating the Degree of Chalking of Exterior Paint Films.

ASTM D2244 - Standard Test Method for Calculation of Color Differences From Instrumentally Measured Color Coordinates.

Miami-Dade County Building Code Compliance Office (BCCO) - Miami-Dade Notice of Acceptance.

** NOTE TO SPECIFIER **  Delete if not required.

USGBC: U.S. Green Building Council LEED® Rating System.

DEFINITIONS

** NOTE TO SPECIFIER **  Retain definitions remaining after this Section has been edited.

Louver Terminology:  Definitions of terms for metal louvers contained in AMCA 501 apply to this Section unless otherwise defined in this Section or in referenced standards.

Horizontal Louver:  Louver with horizontal blades; i.e., the axes of the blades are horizontal.

Vertical Louver:  Louver with vertical blades; i.e., the axes of the blades are vertical.

Drainable-Blade Louver:  Louver with blades having gutters that collect water and drain it to channels in jambs and mullions, which carry it to bottom of unit and away from opening.

Rain-Resistant Louver:  Louver that provides specified wind-driven rain performance, as determined by testing according to AMCA 500-L.

ACTION SUBMITTALS

Submit under provisions of Section 01 30 00.

Product Data:  For each product to be used, including:

Manufacturer's product data including performance data.

Preparation instructions and recommendations.

Storage and handling requirements and recommendations.

Installation methods.

** NOTE TO SPECIFIER **  Ruskin louvers have the potential to contribute points for LEED-NC. Check with the USGBC for specifics on your particular application of Ruskin products. Delete if not required.

Sustainable Documentation Submittals: LEED Rating System.

Certificates for Credit MR 4 - Recycled Content: Increase demand for building products that incorporate recycled content materials, therefore reducing impacts resulting from extraction and processing of new virgin materials.

Percentage of recycled content showing cost and percentage(s) of post-consumer and/or post-industrial content, and the total cost of materials for the louver.

Shop Drawings:

Submit shop drawings indicating materials, construction, dimensions, accessories, and installation details.

Product Schedule:  For louvers.  Use same designations indicated on Drawings.

** NOTE TO SPECIFIER **  Delete selection samples if not required.

Samples:  Submit sample of louver to show frame, blades, bird screen, gutters, downspouts, vertical supports, sill, accessories, finish, and color.

INFORMATIONAL SUBMITTALS

** NOTE TO SPECIFIER **  Coordinate "Qualification Data" Paragraph below with qualification requirements in Division 01 Section "Quality Requirements" and as may be supplemented in "Quality Assurance" Article.

Qualification Data:  For manufacturer and Installer.

Product Test Reports:  For each type of louver, for tests performed by a qualified testing agency.

** NOTE TO SPECIFIER **  Retain "Field quality-control reports" Paragraph below if Contractor is responsible for field quality-control testing and inspecting.

Field quality-control reports.

Sample Warranties:  For manufacturer's warranties.

QUALITY ASSURANCE

Manufacturer Qualifications:

The manufacturer shall have implemented the management of quality objectives, continual improvement, and monitoring of customer satisfaction to assure that customer needs and expectations are met.

Manufacturer shall be International Organization for Standardization (ISO) 9001:2015 accredited.

Louvers approved by the Miami-Dade County BCCO for use in open structures that have the ability to drain water that may penetrate.  Approval based on tests and procedures performed in accordance with BCCO test protocols TAS-201, TAS-202 and TAS-203.

** NOTE TO SPECIFIER **  Insert installer qualifications. Delete if not required.

Installer Qualifications:

USGBC LEED Compliance:  The Work of this section shall be in accordance with applicable portions of the U.S. Green Building Council’s LEED Green Building Rating System. Refer to Divisions 23 and 26 Sections and other related documents bound herein for purposes of complying with this requirement.

Product Qualifications:

Louvers licensed to bear AMCA Certified Ratings Seal.  Ratings based on tests and procedures performed in accordance with AMCA 511 and comply with AMCA Certified Ratings Program.  AMCA Certified Ratings Seal applies to air performance and water penetration ratings.

** NOTE TO SPECIFIER **  Confirm code mandated requirements. ASCE values in lieu of code mandated requirements may be used. Delete if not required.

Louvers shall be factory engineered to withstand the specified seismic loads.

Minimum design loads shall be calculated to comply with ASCE – 7, or local requirements of Authority Having Jurisdiction (AHJ).

** NOTE TO SPECIFIER **  Retain paragraph below if products are required to be certified for 
Credit MR 4.

Recycled Content: Provide louver that incorporate recycled content materials. The louver shall consist of the following recycled content:

Fabricated aluminum recycled content 75% by weight. 10% post-consumer, 15 % pre-consumer.

DELIVERY, STORAGE, AND HANDLING

Store products in manufacturer's unopened packaging until ready for installation.

Store materials in a dry area indoors, protected from damage and in accordance with manufacturer's instructions.

Handling:  Protect materials and finishes during handling and installation to prevent damage.

Store and dispose of solvent-based materials, and materials used with solvent-based materials, in accordance with requirements of local authorities having jurisdiction.

PROJECT CONDITIONS

Maintain environmental conditions (temperature, humidity, and ventilation) within limits recommended by manufacturer for optimum results.  Do not install products under environmental conditions outside manufacturer's absolute limits.

WARRANTY

Manufacturer shall provide standard limited warranty for louver systems for a period of five years (60 months) from date of installation, no more than 60 months after shipment from manufacturing plant. When notified in writing from the Owner of a manufacturing defect, manufacturer shall promptly correct deficiencies without cost to the Owner.

** NOTE TO SPECIFIER Warranty is not available for locales within 1000 feet of coastal waters. Warranty is not available for some exotic colors. Verify finish warranty with manufacturer. Warranty is available for aluminum substrates only. Warranty is not available for sand louvers. Delete if not required.

Manufacturer shall provide 20 year limited warranty for fluoropolymer-based finish on extruded aluminum substrates.

      - Finish coating shall not peel, blister, chip, crack or check.

      - Chalking, fading or erosion of finish when measured by the following tests:

        - Finish coating shall not chalk in excess of 8 numerical ratings when measured in accordance with ASTM D4214.

        - Finish coating shall not change color or fade in excess of 5 NBS units as determined by ASTM D2244 and ASTM D822.

        - Finish coating shall not erode at a rate in excess of 10%/ 5 year as determined by Florida test sample.

    - Manufacturer shall provide a 5 year limited warranty for Class 1 and Class 2 anodized finish on extruded aluminum substrates.

      - Seller warrants the Finish under normal atmospheric conditions.

        - Will not crack, craze, flake or blister

        - Will not change or fade more than (5) Delta-E Hunter units as determined by ASTM method D-2244

        - Will not chalk in excess of ASTM D-4214-07 number (8) rating, determined by the procedure outlined in ASTMD-4214-07 specification test.

      - Any forming or welding must be done prior to finishing.  Post forming or welding will void the warranty.

      - This Warranty applies only if the anodized aluminum product is installed in strict accordance with Seller’s recommended practices and maintained in accordance with AAMA (American Architectural Manufacturers Association) publication number 609 and 610-09 (“Cleaning and Maintenance Guide for Architecturally Finished Aluminum”).

** NOTE TO SPECIFIER **  Delete if finish selected is not PVDF.

PVDF Finish: twenty years.

PRODUCTS

MANUFACTURERS

Acceptable Manufacturer:  Reliable Company; 1300 Enterprise Road, Geneva, Alabama 36340, Tel: 334-684-3914.

** NOTE TO SPECIFIER **  Delete one of the following two paragraphs; coordinate with requirements of Division 1 section on product options and substitutions.

Substitutions:  Not permitted.

Requests for substitutions will be considered in accordance with provisions of Section 01600.

EXTREME PERFORMANCE BLADE LOUVER

Model:  700HZDC as manufactured by Reliable Company.

Description:

Design: Extruded aluminum, wind driven rain resistant, double frame, two-piece blade design with a horizontal front and vertical rear, extreme performance louver.

Miami-Dade Notice of Acceptance Number: 20-1201.01.

Application: The 700HZDC is a double frame extreme performance louver that is Miami Dade Approved. Its two-piece blade design provides protection from wind-driven rain penetration, reducing damage and additional operating expenses. The 700HZDC has visible mullion construction and a horizontal front blade design for architecturally pleasing aesthetics.

Frame Depth: Front fame: 4 inches (102 mm), nominal.

- Rear frame: 3 inches (76 mm), nominal.

Wall Thickness: 0.080 inch (2.0 mm), nominal.

Material: Extruded aluminum, Alloy 6063-T6.

Blades:

Style: Horizontal front blade on a 3.8” (96.52) center to center spacing and vertical rear blade on a 3/4” (1.9) center to center spacing.

Wall Thickness: Front blade 0.080 inch (2.0 mm), nominal. Rear blade .050” (1.3)

Material: Extruded aluminum, Alloy 6063-T6.

Aluminum, 5/8 inches by 0.040 inch (16 mm by 1 mm), expanded and flattened.

Recycled Content: 18% post-consumer. 55% pre-consumer, post-industrial, total 73% by weight.

Performance Data:

AMCA Listing Label Compliance:

AMCA 540 – Test Method for Louvers Impacted by Windborne Debris.

Missile E -Enhanced Protection.

Cycle tested per AMCA 540

AMCA 550 – High Velocity Wind Driven Rain

AMCA Certified Ratings Program

Based on testing 48 inches x 48 inches (1,219 mm x 1,219 mm) size unit in accordance with AMCA 500.

Free Area:  53% nominal.  Free Area Size:  8.49 square feet (0.79 m²).

Water penetration:  Maximum of 0.01 ounce per square foot (3.1 g/m²) of free area at an air flow rate of 803fpm (4.08 m/s) free area velocity when tested for 15 minutes

Pressure Drop: Maximum Intake Pressure Drop at 1,000 fpm:  0.31 inches w.g. (0.08 kPa).

Wind Driven Rain:  Minimum wind-driven rain performance based on testing 39.375 inches x 39.375 inches (1 m x 1 m) core area, 41.375 inches x 44.2 inches (1.04 m x 1.12 m) nominal size unit in accordance with AMCA 500-L.

Wind Velocity:  29 mph (47 kph) & Rainfall Rate:  8 inches/hour (203 mm/hour).

Water Resistance Effectiveness:  99.8% (AMCA Class A)

Free Area Velocity:  1562 feet per minute (7.9 m/s).

Wind Velocity:  50 mph (80 kph) & Rainfall Rate:  8 inches/hour (203 mm/hour).

Water Resistance Effectiveness:  99.8% (AMCA Class A).

Free Area Velocity:  1558 feet per minute (7.9 m/s).

Miami-Dade County Protocols Compliance:

TAS-201 Large and Small Missile Impact Test.

TAS-202 Uniform Static Air Pressure Test.

TAS-203 Cyclic Wind Pressure Test – Maximum Design Pressure Rating +/- 130 psf (6.7 kPa).

** NOTE TO SPECIFIER **  Model is rated for higher velocities with different effectiveness classes – B, C, D.

** NOTE TO SPECIFIER **  Specify required design loading. 20 psf (0.029 kPa) is typical. Insert wind load design required. Equivalent to a 90 mph (145 kph) wind speed. Design Windload:   Incorporate structural supports required to withstand wind load of ±130 psf (6.7 kPa).

** NOTE TO SPECIFIER **  Confirm code mandated seismic requirements. ASCE values in lieu of code mandated requirements may be used. Delete if not required.

Louvers shall be factory engineered to withstand the specified seismic loads.

Minimum design loads shall be calculated to comply with ASCE – 7, or local requirements of Authority Having Jurisdiction (AHJ).

Seismic Performance:  Louvers, including attachments to other construction, shall withstand seismic effects determined by ASCE-7.

ACCESSORIES

** NOTE TO SPECIFIER **  Delete blank-off panel not required.

    - Aluminum Blank-Off Panels:  0.040 (1 mm) aluminum sheet, factory installed with removable fasteners and neoprene gaskets.

    - Insulated Aluminum Blank-Off Panels:  0.040 (1 mm) aluminum sheet, 1 inch (25 mm) aluminum skin insulated core, factory installed with removable fasteners and neoprene gaskets.

    - Insulated Aluminum Blank-Off Panels:  0.040 (1 mm) aluminum sheet, 2 inch (51 mm) aluminum skin insulated core, factory installed with removable fasteners and neoprene gaskets.

** NOTE TO SPECIFIER **  Delete filter rack material not required.

Aluminum Filter Racks:  Formed channel racks to accept standard thick filters.  Unused bottom portion blanked off with 0.040 inch (1 mm) aluminum sheet.

** NOTE TO SPECIFIER **  Delete filter thickness not required.

Filter:  1 inch (25 mm) thick.

Filter:  2 inch (51 mm) thick.

** NOTE TO SPECIFIER **  Delete hinged frame if not required, if hinged section is necessary be aware that Miami Dade NOA, FBC, Florida Building Code Product Approval and AMCA 540 have not conducted tests or established testing criteria for this construction or variation.

** NOTE TO SPECIFIER **  Delete if not required.

Security Bars:

** NOTE TO SPECIFIER **  Delete location not required.

Location: Front.

Location: Rear.

** NOTE TO SPECIFIER ** Delete construction if not required.

Construction: Aluminum 3/4 inch x 1/2 inch (19 mm x 13 mm), welded to louver.

Construction: Aluminum, 3/4 inch x 1/2 inch (19 mm x 13 mm), welded to louver.

** NOTE TO SPECIFIER **  Schedule where bird and insect screens are to be placed: interior or exterior. Install insect screens on intake louvers and bird screens on exhaust louvers. Do not install insect screens on HVAC intake louvers.  Please consult factory representative for additional options regarding screen types.

** NOTE TO SPECIFIER **  Delete bird screen if not required.

Sleeve:

Aluminum:  Aluminum sheet 0.125”thk, 4 side continuous welded

Bird Screen:

** NOTE TO SPECIFIER **  Delete bird screen type not required.

Aluminum:  Aluminum, 5/8 inches by 0.040 inch (16 mm by 1 mm), expanded and flattened.

Aluminum:  Aluminum, 1/2 inch mesh x 0.063 inch (13 mm mesh x 1.6 mm), inter crimp.

Frame:  Removable.

** NOTE TO SPECIFIER ** Delete insect screen if not required. Consult manufacturer for assistance in selecting insect screens.

Insect Screens:

Aluminum: 18-16 mesh, mill finish, .011 inch (0.3 mm) wire.

Frame: Aluminum.

** NOTE TO SPECIFIER **  Not an option with Front flange frame. Delete extended sill if not required.

Extended Sills:

** NOTE TO SPECIFIER **  Delete material not required.

Extruded aluminum, Alloy 6063-T6.  Minimum nominal thickness 0.060 inch (1.5 mm).

Formed Aluminum, Alloy 3003. Minimum nominal thickness 0.081 inch (2.1 mm).

** NOTE TO SPECIFIER **  Delete visible mullions if not required.

Visible Mullions:  Manufacturer's standard horizontal or vertical visible mullions for architectural accent as indicated on drawings.

** NOTE TO SPECIFIER **  Not an option with Front flange frame. Delete extended sill if not required.

FINISHES

** NOTE TO SPECIFIER **  Specify one of the following factory finishes and delete the others.  Mill finish is standard.  Consult Ruskin for assistance in choosing factory finish for specific applications.

Finish: Mill finish.

Finish: 50% PVDF: Finish shall be applied at 1.2 mil total dry film thickness.

Coating shall conform to AAMA 2604, sections 4.2 and 4.3. Apply coating following cleaning and pretreatment. Cleaning:  AA-C12C42R1X.

** NOTE TO SPECIFIER **  Delete finish not required.

Baked Enamel (50% PVDF).

Pearledize 50 (2-coat mica).

20-year finish warranty.

Finish: 70% PVDF: Finish shall be applied at 1.2 mil total dry film thickness.

Coating shall conform to AAMA 2605. Apply coating following cleaning and pretreatment. Cleaning:  AA-C12C42R1X.

** NOTE TO SPECIFIER **  Delete finish not required.

Standard 2-coat.

Pearledize 70 (2-coat mica).

3-coat metallic.

3-coat exotic.

20-year finish warranty.

Color to match-as selected by Architect from manufacturer’s full range (insert color)

EXECUTION

EXAMINATION

Inspect areas to receive louvers.  Notify the Architect of conditions that would adversely affect the installation or subsequent utilization of the louvers.  Do not proceed with installation until unsatisfactory conditions are corrected.

If opening preparation is the responsibility of another installer, notify Architect of unsatisfactory preparation before proceeding.

PREPARATION

Clean opening thoroughly prior to installation.

Prepare surfaces using the methods recommended by the manufacturer for achieving the best result for the substrate under the project conditions.

INSTALLATION

Install louvers at locations indicated on the drawings and in accordance with manufacturer's instructions.

Install louvers plumb, level, in plane of wall, and in alignment with adjacent work.

The supporting structure shall be designed to accommodate the point loads transferred by the louvers when subject to the design wind loads.

** NOTE TO SPECIFIER **  Delete if not required.

Louvers shall be secured to a structural substrate in accordance with Dade County Product Approval Drawings.

Install joint sealants as specified in Section 07 92 00.

** NOTE TO SPECIFIER **  Specify field topcoat if prime coat is specified in PART 2 - PRODUCTS. Delete if not required.

Apply field topcoat within 6 months of application of shop prime coat.  Apply field topcoat as specified in Section 09 91 00.

CLEANING

Clean louver surfaces in accordance with manufacturer's instructions.

Touch-up, repair or replace damaged products before Substantial Completion.

END OF SECTION